## Open Tank or Pressure
Customer: | SNC-Lavalin |  |  |  | Legend:
Customer Site: | Project Rhourde Nouss QH |  |  |  | formulas
Instrument Tag Number: | none |  |  |  | pick list
data entry
Pressure or Level Measurement Using IASPT Transmitters With Pressure Seal
Determine calibrated range (for level) and estimate performance
| EGU | Distance | Temp.
Measurement Engineering Units | mmH2O | Meters | Deg C
Measurement Range Data
Application | Pressure (absolute or gauge)
Enter Upper Range Value | 6000 | mmH2O
Enter Lower Range Value | 0 | mmH2O
Vertical distance between sensor and seal, | 0 | Meters
Nominal specific gravity of meas. Fluid, GL | 1
Specific gravity of seal fill fluid, GS | 0.9072
Process Temperature Range, deg C | High side
Maximum | 300 |  | Max temperature exceeds fluid capability. Select another fluid
Normal | 250
Minimum | 250
Ambient Temperature Range, deg C | High side
Maximum | 40
Normal (or temp. when xmtr is zeroed) | 10
Minimum | -35
Configuration
| High side |  | Seal Type and Size |  | pss_2a-1z11a_a.pdf |  |  |  | Dimensional Print
Capillary Length, ft | 0 |  | High side | PSFLT-.3, Flush 3" direct conn. Flange mount seal |  |  |  |  | dp_020-342_b.pdf
Fill Fluid | DC200, 3CST |  | PIC W35FF, Flush Mount seal for 3" flange connection, direct connected to IDP10, IGP20
Capillary Internal Diameter, inches | 0.027 | [8 empty] | Linls to Dimensional Prints
Transmitter | IDP10 | [8 empty] | dp_020-342_b.pdf
Span Code | C | [8 empty] | dp_020-343_b.pdf
dp_020-345_a.pdf
dp_020-346_a.pdf
dp_020-347_a.pdf
Results Below | [9 empty] | dp_020-348_a.pdf
[6 empty] | Legend: |  |  |  | dp_020-349_a.pdf
[6 empty] | formulas |  |  |  | dp_020-350_a.pdf
The minimum process pressure must be above the fill fluids vapor pressure at the maximum temperature. | Fluid Vapor pressure @ max. temp. |  |  |  |  | pick list |  |  |  | dp_020-351_a.pdf
| 1284.8939 | mm Hg, abs. |  |  |  | data entry
| Calibrated Range: |  | 840 |  | in H2O
Notes: | HW @ min. level, or LRV, |  | mmH2O | 0 | 0
Estimates are for 316ss diaphragms - other materials may have ambient and process temp. errors as much as 3X greater. | HW @ max. level, or URV, |  | mmH2O | 6000 | 236.2205
Performance Estimates:
Temperature effects from normal process and ambient temperatues
to the respective maximum and minimum temperatures.
| Process Temp. Effect |  | Ambient Temp. Effect |  | Head Effect for GS |  | Total Seal SystemTemp. Effect
| for given temp. range |  | for given temp. range |  | chg. over distance d
| mmH2O | % of Span | mmH2O | % of Span | mmH2O | % of Span | mmH2O | % of Span
To Max. Temp | 15.1853 | 0.25309 | 3.1526 | 0.052543 | 0 | 0 | 18.3379 | 0.30563
To Min. Temp | 0 | 0 | -4.7289 | -0.078815 | 0 | 0 | -4.7289 | -0.078815
Response Time Estimates:
Response values are calculated using nominal values for capillary ID and fluid viscosity. Actual times could be as much as 2 X greater or 1/2 X less than shown because of tolerances for capillary ID & viscosity | Ambient Temp, deg C |  |  | -35 | 10 | 40
| 90% response time, seconds |  |  | 0 | 0 | 0
| Time constant, seconds |  |  | 0 | 0 | 0
0.8952
0.9072
Level, Open Tank
Pressure (absolute or gauge)
PSFAD-.2, Direct Conn. flanged off-line seal with 2" diaph
PSFAD-.3, Direct Conn. flanged off-line seal with 3" diaph
PSFAR-.2, Remote flanged off-line seal with 2" diaph
PSFAR-.3, Remote flanged off-line seal with 3" diaph
PSFAR-.4, Remote flanged off-line seal with 4" diaph
PSFES-.2, 2" Flange Extended Remote Pressure Seal
PSFES-.3, 3" Flange Extended Remote Pressure Seal
PSFES-.4, 4" Flange Extended Remote Pressure Seal
PSFLT-.2, Flush 2" direct conn. Flange mount seal
PSFLT-.2, Extended 2" direct conn. Flange mount seal
PSFLT-.3, Flush 3" direct conn. Flange mount seal
PSFLT-.3, Extended 3" direct conn. Flange mount seal
PSFLT-.4, Extended 4" direct conn. Flange mount seal
PSFPS-.2, 2" Flush mount (pancake) remote seal
PSFPS-.3, 3" Flush mount (pancake) remote seal
PSISD = Direct conn. In-Line Saddle Weld connection seal
PSISR = In-Line Saddle Weld connection remote seal | DOW Universal
PSSCD-.2 = 2" Direct connect sanitary seal
PSSCD-.3 = 3" Direct connect sanitary seal
PSSCR-.2, 2" Remote sanitary seal
PSSCR-.3, 3" Remote sanitary seal
PSTAD-.2, Direct Conn. threaded off-line seal with 2" diaph
PSTAD-.3, Direct Conn. threaded off-line seal with 3" diaph
PSTAR-.2, Remote threaded off-line seal with 2" diaph
PSTAR-.3, Remote threaded off-line seal with 3" diaph
PSTAR-.4, Remote threaded off-line seal with 4" diaph
DC200, 10CST
FC77
DC200, 3CST
DC704
Neobee M20
Halocarbon, 6.3
Halocarbon, 4.2
DC550
Syltherm 800
0.027
0.04
0.062
0.118
IDP10
IGP20
IGP10
IAP10
B
C
D
E
0
5
10
15
20
25
30
inH2O | 1
ftH2O | 12
mmH2O | 25.4
cmH2O | 2.54
psi | 27.73
atm | 407.52
Pa | 4021
kPa | 4.021
MPa | 0.004021
torr | 0.5362
mbar | 0.40224 | 500 | 201.12
bar | 402.24
g/cm2 | 0.39444
kg/cm2 | 394.44 | 394.44
inHg | 13.62
mmHg | 0.5362
cmHg | 5.362
dy/cm2 | 2537.81
inches
feet
mm
cm
Meters
Deg. F
Deg C
Note on B16: Fill fluid SG is calculated at the normal ambient temp. value entered below.

## Open or Pressure Summary
Customer | SNC-Lavalin
Site | Project Rhourde Nouss QH
Instrument Tag number | none
Selected Configuration
Transmitter | IDP10
Span Code | C
Fill Fluid | DC200, 3CST
Capillary Length, ft | 0
Capillary Internal Diameter, inches | 0.027
Seal Selected | PSFLT-.3, Flush 3" direct conn. Flange mount seal
PIC W35FF, Flush Mount seal for 3" flange connection, direct connected to IDP10, IGP20
Measurement Range | Lower Range Value | 0 | mmH2O
| Upper Range Value | 6000 | mmH2O
Fluid Vapor pressure @ max. temp. | 1284.8939 | mm Hg, abs.
The minimum process pressure must be above the fill fluids vapor pressure at the maximum temperature.
Warnings:
Max temperature exceeds fluid capability. Select another fluid
Process Conditions and Effects on Performance |  | Output Shift
Process Temperature Range, deg C |  | mmH2O | % of Span
Maximum | 300 | 15.1853 | 0.25309
Normal | 250 | Reference | Reference
Minimum | 250 | 0 | 0
Ambient Temperature Range, deg C |  | mmH2O | % of Span
Maximum | 40 | 3.1526 | 0.052543
Normal (or temp. when xmtr is zeroed) | 10 | Reference | Reference
Minimum | -35 | -4.7289 | -0.078815
Head Effect From Fill Fluid Density Change
Vertical distance between sensor and seal, 0Meters |  | mmH2O | % of Span
Maximum | 40 | 0 | 0
Normal (or temp. when xmtr is zeroed) | 10 | Reference | Reference
Minimum | -35 | 0 | 0
Total Seal SystemTemp. Effect |  | mmH2O | % of Span
Max. process & ambient |  | 18.3379 | 0.30563
Normal operating temperatures |  | Reference | Reference
Min. process & ambient |  | -4.7289 | -0.078815
Response Time Estimates: |  | 90% response time, seconds |  | Time constant, seconds
Ambient Temp, deg C
| -35 | 0 |  | 0
| 10 | 0 |  | 0
| 40 | 0 |  | 0
Seal Displacement at Hot and Cold Temperature Extremes
Seal Displacement, Hot, in^3 |  | 0.05688
Seal Displacement, Cold, in^3 , incl. full scale stroke |  | 0.037844
Max. positive (hot) displacement for seal selected, in^3 |  | 0.29
Max. negative (cold) displacement for seal selected, in^3 |  | -0.1

## Closed Tank or DP
Customer: | SNC-Lavalin |  |  |  | Legend:
Customer Site: | Project Rhourde Nouss QH |  |  |  | formulas
Instrument Tag Number: | none |  |  |  | pick list
data entry
Pressure and Level Measurement Using an IASPT DP Transmitter With Pressure Seal(s)
Determine calibrated range (for level) and estimate performance
| EGU | Distance | Temp.
Measurement Engineering Units | mmH2O | mm | Deg C
Measurement Range Data
Application | Level, Closed Tank
Liquid Level Span, X | 6000 | mm
Liquid Level Offset, Y | 0 | mm |  | Legend:
Vertical distance between seals, d, | 0 | mm |  | formulas
Nominal specific gravity of meas. Fluid, GL | 1 |  |  | pick list
Specific gravity of seal fill fluid, GS | 0.9072 |  |  | data entry
Process Temperature Range, deg C | High side | Low Side
Maximum | 300 | 300 | Temperature exceeds fluid capability. Try another fluid or for assistance contact Foxboro
Normal | 200 | 200
Minimum | 200 | 200
Ambient Temperature Range, deg C | High side | Low Side
Maximum | 40 | 40
Normal (or temp. when xmtr is zeroed) | 10 | 10
Minimum | -35 | -35
Configuration
| High side | Low Side | Seal Type and Size |  | pss_2a-1z11a_a.pdf |  |  |  |  | Dimensional Print
Capillary Length, ft | 0 | 25 | High side | PSFLT-.3, Flush 3" direct conn. Flange mount seal | [5 empty] | dp_020-342_b.pdf
Fill Fluid | DC200, 3CST |  | PIC W35FF, Flush Mount seal for 3" flange connection, direct connected to IDP10, IGP20
Capillary Internal Diameter, inches | 0.027
Transmitter | IDP10
Span Code | D | [8 empty] | Dimensional Print
|  |  | Low side | PSFPS-.3, 3" Flush mount (pancake) remote seal | [5 empty] | dp_020-343_b.pdf
PIC W35FP, Flush Pancake (paddle) seal for 3" flange connection. Previously known as the MP type seal. Best price/performance selection.
Results Below
The minimum process pressure must be above the fill fluids vapor pressure at the maximum temperature. | Fluid Vapor pressure @ max. temp. | [5 empty] | Legend: |  | Linls to Dimensional Prints
| 1284.8939 | mm Hg, abs. |  |  |  |  | formulas |  | dp_020-342_b.pdf
[7 empty] | pick list |  | dp_020-343_b.pdf
[7 empty] | data entry |  | dp_020-345_a.pdf
| Calibrated Range: |  | 8400 |  | in H2O |  |  |  | dp_020-346_a.pdf
Notes: | HW @ min. level, or LRV, |  | mmH2O | 0 | 0 |  |  |  | dp_020-347_a.pdf
Estimates are for 316ss diaphragms - other materials may have ambient and process temp. errors as much as 3X greater. | HW @ max. level, or URV, |  | mmH2O | 6000 | 236.2205 |  |  |  | dp_020-348_a.pdf
dp_020-349_a.pdf
| Performance Estimates: | [7 empty] | dp_020-350_a.pdf
| Temperature effects from normal process and ambient temperatues | [7 empty] | dp_020-351_a.pdf
to the respective maximum and minimum temperatures.
| Process Temp. Effect |  | Ambient Temp. Effect |  | Head Effect for GS |  | Total Seal SystemTemp. Effect |  | Tolerance of Estimate*
| for given temp. range |  | for given temp. range |  | chg. over distance d
| mmH2O | % of Span | mmH2O | % of Span | mmH2O | % of Span | mmH2O | % of Span | +/- | mmH2O
To Max. Temp | 1.0842 | 0.01807 | -8.8772 | -0.14795 | 0 | 0 | -7.793 | -0.12988 | 8.4801
To Min. Temp | 0 | 0 | 13.3158 | 0.22193 | 0 | 0 | 13.3158 | 0.22193 | 3.6089
* Tolarance for process and ambient temp. effects due to residual variation in seal characteristics.
Response Time Estimates:
Response values are calculated using nominal values for capillary ID and fluid viscosity. Actual times could be as much as 2 X greater or 1/2 X less than shown because of tolerances for capillary ID & viscosity | Ambient Temp, deg C |  |  | -35 | 10 | 40
| 90% response time, seconds |  |  | 0.3089 | 0.093797 | 0.051257
| Time constant, seconds |  |  | 0.1343 | 0.040781 | 0.022285
0.8952
0.9072
Level, Closed Tank
Differential Pressure
No seal | No seal
PSFAR-.2, Remote flanged off-line seal with 2" diaph | PSFAR-.2, Remote flanged off-line seal with 2" diaph
PSFAR-.3, Remote flanged off-line seal with 3" diaph | PSFAR-.3, Remote flanged off-line seal with 3" diaph
PSFAR-.4, Remote flanged off-line seal with 4" diaph | PSFAR-.4, Remote flanged off-line seal with 4" diaph
PSFES-.2, 2" Flange Extended Remote Pressure Seal | PSFES-.2, 2" Flange Extended Remote Pressure Seal
PSFES-.3, 3" Flange Extended Remote Pressure Seal | PSFES-.3, 3" Flange Extended Remote Pressure Seal
PSFES-.4, 4" Flange Extended Remote Pressure Seal | PSFES-.4, 4" Flange Extended Remote Pressure Seal
PSFLT-.2, Flush 2" direct conn. Flange mount seal | PSFPS-.2, 2" Flush mount (pancake) remote seal
PSFLT-.2, Extended 2" direct conn. Flange mount seal | PSFPS-.3, 3" Flush mount (pancake) remote seal
PSFLT-.3, Flush 3" direct conn. Flange mount seal | PSISR = In-Line Saddle Weld connection remote seal
PSFLT-.3, Extended 3" direct conn. Flange mount seal | PSSCR-.2, 2" Remote sanitary seal
PSFLT-.4, Extended 4" direct conn. Flange mount seal | PSSCR-.3, 3" Remote sanitary seal
PSFPS-.2, 2" Flush mount (pancake) remote seal | PSTAR-.2, Remote threaded off-line seal with 2" diaph
PSFPS-.3, 3" Flush mount (pancake) remote seal | PSTAR-.3, Remote threaded off-line seal with 3" diaph
PSISR = In-Line Saddle Weld connection remote seal | PSTAR-.4, Remote threaded off-line seal with 4" diaph
PSSCR-.2, 2" Remote sanitary seal
PSSCR-.3, 3" Remote sanitary seal
PSTAR-.2, Remote threaded off-line seal with 2" diaph
PSTAR-.3, Remote threaded off-line seal with 3" diaph
PSTAR-.4, Remote threaded off-line seal with 4" diaph
DC200, 10CST
FC77
DC200, 3CST
DC704
Neobee M20
Halocarbon, 4.2
Halocarbon, 6.3
DC550
Syltherm 800
0.027
0.04
0.062
0.118
IDP10
IGP20
IGP10
IAP10
B
C
D
E
0
5
10
15
20
25
30
inH2O | 1
ftH2O | 12
mmH2O | 25.4
cmH2O | 2.54
psi | 27.73
atm | 407.52
Pa | 4021
kPa | 4.021
MPa | 0.004021
torr | 0.5362
mbar | 0.40224 | 500 | 201.12
bar | 402.24
g/cm2 | 0.39444
kg/cm2 | 394.44 | 394.44
inHg | 13.62
mmHg | 0.5362
cmHg | 5.362
dy/cm2 | 2537.81
inches
feet
mm
cm
Meters
Deg. F
Deg C
Note on B16: Fill fluid SG is calculated at the normal ambient temp. value entered below.

## Closed or DP summary
Customer | SNC-Lavalin
Site | Project Rhourde Nouss QH
Instrument Tag number | none
Selected Configuration
Transmitter | IDP10
Span Code | D
Fill Fluid | DC200, 3CST
High Side Capillary Length, ft | 0
Low Side Capillary Length, ft | 25
Capillary Internal Diameter, inches | 0.027
Seal Selected, High Side | PSFLT-.3, Flush 3" direct conn. Flange mount seal
PIC W35FF, Flush Mount seal for 3" flange connection, direct connected to IDP10, IGP20
Seal Selected, Low Side | PSFPS-.3, 3" Flush mount (pancake) remote seal
PIC W35FP, Flush Pancake (paddle) seal for 3" flange connection. Previously known as the MP type seal. Best price/performance selection.
Measurement Range | Lower Range Value | 0 | mmH2O
| Upper Range Value | 6000 | mmH2O
Seal fill fluid vapor pressure at maximum temperature | 1284.8939 | mm Hg, abs. | The minimum process pressure must be above the fill fluids vapor pressure at the maximum temperature.
Warnings:
At maximum process temperature: | Temperature exceeds fluid capability. Try another fluid or for assistance contact Foxboro
At minimum process temperature:
At maximum ambient temperature:
At minimum ambient temperature:
Process Conditions and Effects on Performance |  | High Side | Low Side | Output Shift
| Process Temperature Range, deg C |  |  | mmH2O | % of Span
| Maximum | 300 | 300 | 1.0842 | 0.01807
| Normal | 200 | 200 | Reference | Reference
| Minimum | 200 | 200 | 0 | 0
| Ambient Temperature Range, deg C |  |  | mmH2O | % of Span
| Maximum | 40 | 40 | -8.8772 | -0.14795
| Normal (or temp. when xmtr is zeroed) | 10 | 10 | Reference | Reference
| Minimum | -35 | -35 | 13.3158 | 0.22193
Head Effect From Fill Fluid Density Change
Vertical distance between seals, d, 0mm |  |  |  | mmH2O | % of Span
| To Maximum Ambient Temperature |  |  | 0 | 0
| Normal (or temp. when xmtr is zeroed) |  |  | Reference | Reference
| To Minimum Ambient Temperature |  |  | 0 | 0
Tolerance of Estimate
Estimated Total Seal SystemTemperature Effect |  |  |  | mmH2O | % of Span | +/- | mmH2O
| Max. process & ambient |  |  | -7.793 | -0.12988 |  | 8.4801
| Normal operating temperatures |  |  | Reference | Reference |  | Reference
| Min. process & ambient |  |  | 13.3158 | 0.22193 |  | 3.6089
Response Time Estimates: |  | 90% response time, seconds |  | Time constant, seconds
Ambient Temp, deg C
| -35 | 0.3089 |  | 0.1343
| 10 | 0.093797 |  | 0.040781
| 40 | 0.051257 |  | 0.022285
Seal Displacement at Hot and Cold Temperature Extremes
|  | High side | Low side
| Seal Displacement, Hot, in^3 | 0.05688 | 0.058564
| Seal Displacement, Cold, in^3 , incl. full scale stroke | 0.02878 | 0.019613
| Max. positive (hot) displacement for seal selected, in^3 | 0.29 | 0.29
| Max. negative (cold) displacement for seal selected, in^3 | -0.1 | -0.12

## Seal Properties (hidden)
| Configurator selection text | Volume Spring Rate, in. H2O/in3 |  | Max.positive displacement, in3. | Max.negative displacement, in3.
Seal type |  |  | Seal Volume.,in3 |  |  |  | Seal discription
None | No seal | 0 | 0 | 0 | 0
PSFAD-.2 | PSFAD-.2, Direct Conn. flanged off-line seal with 2" diaph | 800 | 0.45 | 0.06 | -0.06 | dp_020-346_a.pdf | PIC W24B or Conoflow 300B series flange attached seals. Recommended for large pressure ranges or minimal temperature variation. Available in a wide variety of materials and process connection sizes. Was Auxillary Spec. PES-SC, etc. For IGP10 & IAP10
PSFAD-.3 | PSFAD-.3, Direct Conn. flanged off-line seal with 3" diaph | 230 | 0.242 | 0.14 | -0.14 | dp_020-346_a.pdf | PIC W29B or Conoflow 330B series flange attached seals. Recommended for applications with moderate temperature variation. Available in a wide variety of materials and process connection sizes. For IGP10 & IAP10. Same as Auxillary Spec. PES-SC, etc.,except larger diaphragm for better temp.capability.
PSFAR-.2 | PSFAR-.2, Remote flanged off-line seal with 2" diaph | 800 | 0.19 | 0.06 | -0.06 | dp_020-345_a.pdf | PIC W24B or Conoflow 300B series flange attached seals. Recommended for large pressure ranges or minimal temperature variation. Available in a wide variety of materials and process connection sizes. Was PES-SC, etc.
PSFAR-.3 | PSFAR-.3, Remote flanged off-line seal with 3" diaph | 230 | 0.19 | 0.14 | -0.14 | dp_020-345_a.pdf | PIC W29B or Conoflow 330B series flange attached seals. Recommended for DP applications with moderate temperature variation. Available in a wide variety of materials and process connection sizes. Same as Auxillary Spec. PES-SC, etc.,except larger diaphragm for better temp.capability.
PSFAR-.4 | PSFAR-.4, Remote flanged off-line seal with 4" diaph | 30 | 0.4 | 0.25 | -0.25 | dp_020-345_a.pdf | PIC W41B or Conoflow 600B series flange attached seals. Recommended for small pressure ranges with large temperature variation. Available in a wide variety of materials and process connection sizes. Same as Aux. Spec. PES-SC, etc except 4" diaphragm for optimal temp. capability.
PSFES-.2 | PSFES-.2, 2" Flange Extended Remote Pressure Seal | 1400 | 0.054 | 0.05 | -0.03 | dp_020-343_b.pdf | Extended seal for 2" flange connection. Allows diaph to extend through mounting nozzle to be flush with inside of tank wall, eliminating cavities where plugging could occur. Small diameter diaph.s' displacement capability limits temperature range and/or capillary length.
PSFES-.3 | PSFES-.3, 3" Flange Extended Remote Pressure Seal | 450 | 0.099 | 0.14 | -0.075 | dp_020-343_b.pdf | Extended seal for 3" flange connection. Allows diaph to extend through mounting nozzle to be flush with inside of tank wall, eliminating cavities where plugging could occur.
PSFES-.4 | PSFES-.4, 4" Flange Extended Remote Pressure Seal | 30 | 0.48 | 0.29 | -0.12 | dp_020-343_b.pdf | Extended seal for 4" flange connection. Allows diaph to extend through mounting nozzle to be flush with inside of tank wall, eliminating cavities where plugging could occur. Large diaph diameter provides optimal performance over a wide temperature range.
PSFLT-.2X | PSFLT-.2, Extended 2" direct conn. Flange mount seal | 1333 | 0.06 | 0.05 | -0.03 | dp_020-342_b.pdf | Extended seal for 2" flange connection, direct connected to IDP10, IGP20. Allows diaph to extend through mounting nozzle to be flush with inside of tank wall, eliminating cavities where plugging could occur. Small diameter diaph.s' displacement capability limits temperature range.
PSFLT-.2 | PSFLT-.2, Flush 2" direct conn. Flange mount seal | 217 | 0.092359 | 0.08 | -0.04 | dp_020-342_b.pdf | PIC W24FF, Flush Mount seal for 2" flange connection, direct connected to IDP10, IGP20
PSFLT-.3X | PSFLT-.3, Extended 3" direct conn. Flange mount seal | 450 | 0.11 | 0.14 | -0.075 | dp_020-342_b.pdf | Extended seal for 3" flange connection, direct connected to IDP10, IGP20. Allows diaph to extend through mounting nozzle to be flush with inside of tank wall, eliminating cavities where plugging could occur.
PSFLT-.3 | PSFLT-.3, Flush 3" direct conn. Flange mount seal | 60 | 0.17629 | 0.29 | -0.1 | dp_020-342_b.pdf | PIC W35FF, Flush Mount seal for 3" flange connection, direct connected to IDP10, IGP20
PSFLT-.4X | PSFLT-.4, Extended 4" direct conn. Flange mount seal | 30 | 0.5 | 0.29 | -0.12 | dp_020-342_b.pdf | Extended seal for 4" flange connection, direct connected to IDP10, IGP20. Allows diaph to extend through mounting nozzle to be flush with inside of tank wall, eliminating cavities where plugging could occur. Large diaph diameter provides optimal performance over a wide temperature range.
PSFPS-.2 | PSFPS-.2, 2" Flush mount (pancake) remote seal | 365 | 0.082 | 0.08 | -0.06 | dp_020-343_b.pdf | PIC W24FP, Flush Pancake (paddle) seal for 2" flange connection. (MP type for 2" flange connection)
PSFPS-.3 | PSFPS-.3, 3" Flush mount (pancake) remote seal | 60 | 0.17 | 0.29 | -0.12 | dp_020-343_b.pdf | PIC W35FP, Flush Pancake (paddle) seal for 3" flange connection. Previously known as the MP type seal. Best price/performance selection.
PSISD-.2 | PSISD = Direct conn. In-Line Saddle Weld connection seal | 800 | 0.35 | 0.06 | -0.06 | dp_020-350_a.pdf | PSISD = Direct conn. In-Line Saddle Weld connection seal. Was PES-SJ
PSISR-.2 | PSISR = In-Line Saddle Weld connection remote seal | 800 | 0.35 | 0.06 | -0.06 | dp_020-349_a.pdf | PSISR = In-Line Saddle Weld connection remote seal. Was PES-SJ
PSSCR-.2 | PSSCR-.2, 2" Remote sanitary seal | 1600 | 0.087 | 0.045 | -0.045 |  | PIC S19 or Conoflow 700_-_2 seal for 2" Sanitary connection. Was PES-CST, etc.
PSSCR-.3 | PSSCR-.3, 3" Remote sanitary seal | 220 | 0.22 | 0.12 | -0.12 |  | PIC S29 seal for 3" Sanitary connection. Was PES-CST, etc.
PSTAD-.2 | PSTAD-.2, Direct Conn. threaded off-line seal with 2" diaph | 800 | 0.35 | 0.06 | -0.06 | dp_020-351_a.pdf | PIC W24A or Conoflow 300A series thread attached seals. Recommended for large pressure ranges or minimal temperature variation. Available in a wide variety of materials and process connection sizes. Was PES-SB, etc. For IGP10 & IAP10
PSTAD-.3 | PSTAD-.3, Direct Conn. threaded off-line seal with 3" diaph | 230 | 0.242 | 0.14 | -0.14 | dp_020-351_a.pdf | PIC W29A or Conoflow 330A series thread attached seals. Recommended for applications with moderate temperature variation. Available in a wide variety of materials and process connection sizes. For IGP10 & IAP10
PSTAR-.2 | PSTAR-.2, Remote threaded off-line seal with 2" diaph | 800 | 0.19 | 0.06 | -0.06 | dp_020-348_a.pdf | PIC W24A or Conoflow 300A series thread attached seals. Recommended for large pressure ranges or minimal temperature variation. Available in a wide variety of materials and process connection sizes. Was PES-SB, etc.
PSTAR-.3 | PSTAR-.3, Remote threaded off-line seal with 3" diaph | 230 | 0.19 | 0.14 | -0.14 | dp_020-348_a.pdf | PIC W29A or Conoflow 330A series thread attached seals. Recommended for DP applications with moderate temperature variation. Available in a wide variety of materials and process connection sizes.
PSTAR-.4 | PSTAR-.4, Remote threaded off-line seal with 4" diaph | 30 | 0.4 | 0.25 | -0.25 | dp_020-347_a.pdf | PIC W41A or Conoflow 600A series thread attached seals. Recommended for small pressure ranges with large temperature variation. Available in a wide variety of materials and process connection sizes.
PSSST-.2 | PSSST-.2, Sanitary mini tank spud seal, direct connected to IDP10, IGP20 | 1333 | 0.06 | 0.05 | -0.03 | dp_020-347_a.pdf | PIC S19CE, Sanitary Mini Tank Spud Seal for bolted, direct connect to an IDP10 or IGP20
PSSST-.4 | PSSST-.4, Sanitary tank spud seal, direct connected to IDP10, IGP20 | 450 | 0.11 | 0.14 | -0.075 | dp_020-347_a.pdf | PIC S36CE, Sanitary Tank Spud Seal for bolted, direct connect to an IDP10 or IGP20
PSSSR-.2 | PSSSR-.2, Remote Sanitary mini tank spud seal | 1400 | 0.054 | 0.05 | -0.03 |  | PIC S19CE, Sanitary Mini Tank Spud Seal for bolted, direct connect to an IDP10 or IGP20
PSSSR-.4 | PSSST-.4, Remote Sanitary tank spud seal | 450 | 0.099 | 0.14 | -0.075 |  | PIC S36CE, Sanitary Tank Spud Seal for bolted, direct connect to an IDP10 or IGP20
PSSCT-.2 | PSSCT-.2, 2" Direct connect sanitary seal | 1600 | 0.095 | 0.045 | -0.045 |  | PIC S19 seal for 2" Sanitary Seal for bolted direct connect to an IDP10 or IGP20
PSSCT-.3 | PSSCT-.3, 3" Direct connect sanitary seal | 220 | 0.23 | 0.12 | -0.12 |  | PIC S29 seal for 3" Sanitary Seal for bolted direct connect to an IDP10 or IGP20
PSSCR-.4 | PSSCR-.4, 4" Remote sanitary seal | 30 | 0.4 | 0.25 | -0.25 |  | PIC S41 seal for 4" Sanitary connection. Was PES-CST, etc.

## Fill Fluid Properties
|  |  |  | Viscosity correction constants |  |  |  | Constants for vapor
Model Code | Fill Fluid |  | Thrmal xpan |  |  | Constants for SG calc |  | pressure calculation |  | Temperature Range
suffix |  |  | in3/in3/degF | BL | AL | m | b | A | B | Minimum | Maximum
1 | DC200, 10CST |  | 0.0006 | 3680.2697 | 0.0098204 | -0.0006 | 0.983 | 8.721 | 3830.0925 | -40 | 450
3 | DC200, 3CST |  | 0.000628 | 3214.8637 | 0.0066747 | -0.0006 | 0.9372 | 8.6333 | 3165.5056 | -40 | 300
8 | DC550 |  | 0.00042 | 12634.4508 | 7.965e-09 | -0.00038 | 1.1 | 11.8127 | 6461.0234 | -40 | 580
4 | DC704 |  | 0.000486 | 7843.7188 | 1.875e-05 | -0.0005 | 1.1078 | 11.025 | 5570 | 32 | 580
2 | FC77 |  | 0.0008 | 3249.5638 | 0.0033953 | -0.0014 | 1.877 | 8.0915 | 1928 | -75 | 180
7 | Halocarbon, 4.2 |  | 0.00055 | 4799.5614 | 0.0014713 | -0.0009 | 1.942 | 8.08 | 2625 | -40 | 400
6 | Halocarbon, 6.3 |  | 0.00055 | 5418.0164 | 0.00074971 | -0.0009 | 1.962 | 7.898 | 2586.62 | -40 | 400
5 | Neobee M20 |  | 0.000513 | 4365.419 | 0.0030088 | -0.0004 | 0.9519 | 9.122 | 3918.3223 | 0 | 400
9 | Syltherm 800 |  | 0.0006 | 4117.9248 | 0.0043494 | -0.0006 | 0.96 | 6.7163 | 1828.3044 | -40 | 450
Vapor pressure estimate
log p = A-(b/(t+273))
Solve for Coefficients A and B when vapor pressure is known at 2 temperatures
T low, C | 40 |  |  | 0.0021142 |  |  | 2.851 | coef B |  |  | 133.322
T hi, C | 200 |  |  | 0.0031949 |  |  | 0.8751 | -1828.3044 | -0.00054695 |  | 1000
Vp@Tlow | 7.5006 | mm Hg |  |  |  |  | coef A | 6.7163 |  |  | 7.5006
Vp@Thi | 709.5603 | mm Hg |  | 3.8866
Coef B = | 1828.3044 |  |  | 1527.4236 |  | 0.65735 | 4.5431
Coef A = | 6.7163 |  |  |  |  | -0.99337 | 0.10154
Note: Coeffecients are calculated in terms of degrees Kelvin.
Temperature Correction for Absolute Viscosity
Andrades equation
u = AL exp BL/T
From two known values of viscosity constants AL and BL can be determined
BL = (T1 * T2 * ln(u1/u2))/(T2 - T1)
AL = u1/exp (BL/T1) | [7 empty] | 0.56497
0.53476
u1= | 24369.4 | [6 empty] | 0.030213
u2= | 133.5 | [6 empty] | 0.00027466
T1, F = | -20.2 | [6 empty] | 0.056498
T2, F = | 77 | [6 empty] | 0.00051362
AL = | 7.965e-09 |  | 459.67
BL = | 12634.4508
Note: Coeffecients are calculated in terms of degrees Rankine. | [7 empty] | 1.00042*
1.068
125
133.5

## calcclosed (hidden)
TEMPERATURE EFFECTS | Hot |  |  |  | Cold
| ambient |  | process |  | ambient |  | process
| Hi side | low side | Hi side | low side | Hi side | low side | Hi side | low side
CAPILLARY ID., INCHES | 0.027 | 0.027 | 0 | 0 | 0.027 | 0.027 | 0
CAPILLARY LENGTH, FEET | 0 | 25 | 0 | 0 | 0 | 25 | 0
CAPILLARY VOL., IN^3 | 0 | 0.17177 | 0 | 0 | 0 | 0.17177 | 0
SEAL VOL. IN^3 | 0 | 0 | 0.17629 | 0.17 | 0 | 0 | 0.17629 | 0.17
TRANS.VOL., IN^3 | 0.061 | 0.061 | 0 | 0 | 0.061 | 0.061 | 0
THERMAL VOL.EXP, %/degF | 0.000628 | 0.000628 | 0.000628 | 0.000628 | 0.000628 | 0.000628 | 0.000628 | 0.000628
DIAPH. VOL. K, (IN H2O/IN^3) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
TEMP ERROR, inches H2O over normal operating range | 0.12412 | 0.47361 | 1.1957 | 1.153 | -0.18618 | -0.71042 | 0 | 0
TEMP ERROR, inches H2O, from 70F ref. | 0.078148 | 0.2982 | 3.3347 | 3.2156 | -0.23215 | -0.88584 | 2.139 | 2.0626
TEMP.ERROR/50 DEG.F, in. H2O (not used) | 0.44706 | 0.32361
Full scale volume stroke of selected sensor, in^3 | [6 empty] | -0.003
| 0.062302 | 0.23774 | 0.23187 | 0.22359 | 0.057131 | 0.218 | 0.21194 | 0.20438
FILL VOL. EXPANSION/Contraction, in^3 | 0.0013025 | 0.00497 | 0.055578 | 0.053594 | -0.0038691 | -0.014764 | 0.035649 | 0.034377
| 0.33386 | -0.14208
System response
capillary length |  | 25
|  | 25 | [6 empty] | High side | Low side
capillary id |  | 0.027 |  |  |  | Seal Displacement, Hot, in^3 |  |  | 0.05688 | 0.058564
xmtr vol k, psi/in^3 |  | 300000 |  | IDP10D |  | Seal Displacement, Cold, in^3 , incl. full scale stroke |  |  | 0.02878 | 0.019613
seal vol k, psi/in^3 |  | 4.3274 |  |  |  | Max. positive (hot) displacement for seal selected, in^3 |  |  | 0.29 | 0.29
temp. min |  | -31 |  |  |  | Max. negative (cold) displacement for seal selected, in^3 |  |  | -0.1 | -0.12
temp., mid |  | 50
temp. max |  | 104
BL |  | 3214.8637
AL |  | 0.0066747
Vis @ min temp |  | 12.0635
Vis @ mid temp |  | 3.6631
Vis @ max temp |  | 2.0017
|  | 90%res | time constant
temp= | -31 | 0.3089 | 0.1343
temp= | 50 | 0.093797 | 0.040781
temp= | 104 | 0.051257 | 0.022285
Seal Fluid Head Effect |  |  | m | b
Specific gravity @ min. ambient temp | 0.9558 | 95.58 | -0.0006 | 0.9372
Specific gravity @ normal. ambient temp | 0.9072 | 90.72
Specific gravity @ max. ambient temp | 0.8748 | 87.48
Specific gravity @ 70 deg F ambient temp | 0.8952 | 89.52
-0.0006
Head Effect, normal to max. temp. | 0 | 0 | 0
Head Effect, normal to min. temp. | 0
0
Fluid Vapor pressure at max temperature | 1284.8939 | log p = A-(b/(t+273)) |  |  | y = 0.0005x2.6284
max temp. | 300
p =10^ (A-(b/(t+273)))
Unit Conversions
EGU | 404 | in H2O
atm | 407.52 | 164638.08
bar | 402.24 | 162504.96
cmHg | 5.362 | 2166.248
dy/cm2 | 2537.81 | 1025275.24
g/cm2 | 0.39444 | 159.3538
inHg | 13.62 | 5502.48
kg/cm2 | 394.44 | 159353.76
kPa | 4.021 | 1624.484
mbar | 0.40224 | 162.505
mmHg | 0.5362 | 216.6248
MPa | 4021 | 1624484
Pa | 0.004021 | 1.6245
psi | 27.73 | 11202.92
torr | 0.5362 | 216.6248
cmH2O | 0.3937 | 159.0551
ftH2O | 12 | 4848
inH2O | 1 | 404
mmH2O | 0.03937 | 15.9055
Distance
cm | 0.3937 | 0.3937 | 2.54
feet | 12 | 0.083333
inches | 1 | 1
Meters | 39.3701 | 39.3701 | 0.0254
mm | 0.03937 | 0.03937 | 25.4
temperature |  |  |  | High side | Low Side
Deg F | 1 | 0 | b14 | 572 | 572 | c14
Deg C | 1.8 | 32 | b15 | 392 | 392 | c15
|  |  | b16 | 392 | 392 | c16
|  |  |  | High side | Low Side
|  |  | b18 | 104 | 104 | c18
|  |  | b19 | 50 | 50 | c19
|  |  | b20 | -31 | -31 | c20

## calc (hidden)
TEMPERATURE EFFECTS | Hot |  |  |  | Cold
| ambient |  | process |  | ambient | process
| Hi side |  | Hi side |  | Hi side | Hi side
CAPILLARY ID., INCHES | 0.027 |  | 0 |  | 0.027 | 0
CAPILLARY LENGTH, FEET | 0 |  | 0 |  | 0 | 0
CAPILLARY VOL., IN^3 | 0 |  | 0 |  | 0 | 0
SEAL VOL. IN^3 | 0 |  | 0.17629 |  | 0 | 0.17629
TRANS.VOL., IN^3 | 0.061 |  | 0 |  | 0.061 | 0
THERMAL VOL.EXP, %/degF | 0.000628 |  | 0.000628 |  | 0.000628 | 0.000628
DIAPH. VOL. K, (IN H2O/IN^3) | 60 |  | 60 |  | 60 | 60
TEMP ERROR, inches H2O over normal operating range | 0.12412 |  | 0.59785 |  | -0.18618 | 0
TEMP ERROR, inches H2O, from 70F ref. | 0.078148 |  | 3.3347 |  | -0.23215 | 2.7368
TEMP.ERROR/50 DEG.F, in. H2O (not used) | 0.44706
Full scale volume stroke of selected sensor, in^3 | [5 empty] | -0.0039
| 0.062302 |  | 0.23187 |  | 0.057131 | 0.22191
FILL VOL. EXPANSION/Contraction, in^3 | 0.0013025 |  | 0.055578 |  | -0.0038691 | 0.045613
0.36098
System response
capillary length |  | 0 |  |  |  |  | High side
0
capillary id |  | 0.027
xmtr vol k, psi/in^3 |  | 7930 |  | IDP10C
seal vol k, psi/in^3 |  | 2.1637
temp. min |  | -31
temp., mid |  | 50
temp. max |  | 104
BL |  | 3214.8637
AL |  | 0.0066747
Vis @ min temp |  | 12.0635
Vis @ mid temp |  | 3.6631
Vis @ max temp |  | 2.0017
|  | 90%res | time constant
temp= | -31 | 0 | 0
temp= | 50 | 0 | 0
temp= | 104 | 0 | 0
Seal Fluid Head Effect |  |  | m | b
Specific gravity @ min. ambient temp | 0.9558 | 95.58 | -0.0006 | 0.9372
Specific gravity @ normal. ambient temp | 0.9072 | 90.72
Specific gravity @ max. ambient temp | 0.8748 | 87.48
Specific gravity @ 70 deg F ambient temp | 0.8952 | 89.52
-0.0006
Head Effect, normal to max. temp. | 0 | 0 | 0
Head Effect, normal to min. temp. | 0
0
Fluid Vapor pressure at max temperature | 1284.8939 | log p = A-(b/(t+273)) |  |  | y = 0.0005x2.6284
max temp. | 300
p =10^ (A-(b/(t+273)))
Unit Conversions
EGU | 24 | in H2O
atm | 407.52 | 9780.48
bar | 402.24 | 9653.76
cmHg | 5.362 | 128.688
dy/cm2 | 2537.81 | 60907.44
g/cm2 | 0.39444 | 9.4666
inHg | 13.62 | 326.88
kg/cm2 | 394.44 | 9466.56
kPa | 4.021 | 96.504
mbar | 0.40224 | 9.6538
mmHg | 0.5362 | 12.8688
MPa | 4021 | 96504
Pa | 0.004021 | 0.096504
psi | 27.73 | 665.52
torr | 0.5362 | 12.8688
cmH2O | 0.3937 | 9.4488
ftH2O | 12 | 288
inH2O | 1 | 24
mmH2O | 0.03937 | 0.94488
Distance
cm | 0.3937 | 0.3937 | 2.54
feet | 12 | 0.083333
inches | 1 | 1
Meters | 39.3701 | 39.3701 | 0.0254
mm | 0.03937 | 0.03937 | 25.4
temperature |  |  |  | High side
Deg F | 1 | 0 | b14 | 572
Deg C | 1.8 | 32 | b15 | 482
|  |  | b16 | 482
High side
|  |  | b18 | 104
|  |  | b19 | 50
|  |  | b20 | -31

## Xmtr Properties (hidden)
Transmitter Properties
| Vol. K, psi/in^3 | Cavity Vol | URL |  | Full Scale Displacement
iap10c | 300000 | 0.024 | 840 | 1.68 | 9e-05
iap10d | 300000 | 0.024 | 8400 |  | 9e-05
iap10e | 300000 | 0.024 | 84000 |  | 9e-05
iap20b | 7930 | 0.061 | 200 | 0.4 | 0.0023
iap20c | 7930 | 0.061 | 840 | 1.68 | 0.0039
iap20d | 300000 | 0.061 | 8400 |  | 0.003
iap20e | 300000 | 0.061 | 84000 |  | 0.003 | 3029.2102
idp10b | 7930 | 0.061 | 200 | 0.4 | 0.0023
idp10c | 7930 | 0.061 | 840 | 1.68 | 0.0039
idp10d | 300000 | 0.061 | 8400 |  | 0.003
idp10e | 300000 | 0.061 | 84000 |  | 0.003
igp10c | 300000 | 0.024 | 840 | 1.68 | 9e-05
igp10d | 300000 | 0.024 | 8400 |  | 9e-05
igp10e | 300000 | 0.024 | 84000 |  | 9e-05
igp20b | 7930 | 0.061 | 200 | 0.4 | 0.0023
igp20c | 7930 | 0.061 | 840 | 1.68 | 0.0039
igp20d | 300000 | 0.061 | 8400 |  | 0.003
igp20e | 300000 | 0.061 | 84000 |  | 0.003